## Slide 1
Hot-Air Recirculation in a Cooling-Tower Array
A steady RANS parametric study and a physics-informed field surrogate
Computational Fluid Dynamics | Physics-Informed Machine Learning

## Slide 2
The problem: hot-air recirculation
When plumes bend back onto neighbouring intakes, the whole plant loses cooling capacity
Cooling towers reject heat by discharging warm air upward.
In a tight array, wind can bend one unit’s plume down onto the intakes of the next.
Ingested exhaust raises intake temperature and cuts thermal capacity.
The outcome is a tug-of-war: buoyancy lifts the plume, wind bends it over.
Plan and elevation of the six-unit array in a crosswind

## Slide 3
Approach: from solver to a fast field model
1
CFD sweep
Seven steady RANS cases in ANSYS Fluent over wind speed and discharge velocity, with buoyancy.
→
2
Field data
Full 3D velocity and temperature extracted per case, plus per-tower recirculation.
→
3
Physics-informed surrogate
A network maps operating point to the full field, constrained to conserve mass.
One fixed geometry across the sweep, so the surrogate sees a single consistent domain.

## Slide 4
The case and the mesh
6
cooling-tower cells
105,676
tetrahedral cells
600
iterations per case
<0.1%
energy balance error
Domain 280 x 140 x 80 m atmospheric block, wind along +x.
Towers 12 x 12 m footprint, 10 m tall, three columns by two rows.
Physics realizable k-epsilon, incompressible-ideal-gas density under gravity.
Discharge 313 K warm air into a 298 K ambient.

## Slide 5
Parametric sweep
Seven operating points spanning the wind and discharge design space
Case | Wind U | Discharge V | V / U | Mean RC | Worst RC
c1 | 3.0 | 6.0 | 2.0 | 0.61% | 2.41%
c2 | 1.5 | 6.0 | 4.0 | 0.24% | 0.83%
c3 | 6.0 | 6.0 | 1.0 | 1.22% | 1.62%
c4 | 3.0 | 3.0 | 1.0 | 0.59% | 1.38%
c5 | 3.0 | 9.0 | 3.0 | 0.14% | 0.55%
c6 | 1.5 | 3.0 | 2.0 | 0.27% | 1.33%
c7 | 6.0 | 9.0 | 1.5 | 0.89% | 1.88%
Units: m/s. RC is the intake temperature rise as a fraction of the discharge excess.
Key variable
V / U
the plume bend-over ratio
Low V/U wind bends plumes onto intakes.
High V/U plumes rise clear.

## Slide 6
Temperature fields: the regime change
Wind-dominated (c3): plumes bend over and warm the downwind wake
Buoyancy-dominated (c5): plumes rise steeply, intakes stay cool
Same geometry, opposite outcome: the wind-to-plume balance decides whether exhaust is re-ingested.

## Slide 7
Flow diagnostics (wind-dominated case)
Velocity magnitude
Static pressure
Turbulent kinetic energy
Wakes low-speed recirculation forms right behind each tower.
Pressure stagnation high on the windward face, suction lows in the wakes.
Turbulence concentrates in the plume shear layers, where entrainment is strongest.

## Slide 8
Recirculation follows the bend-over ratio
1.62%
worst-tower recirculation (strong wind, c3)
0.14%
array mean, strong plume in light wind (c5)
Modest magnitudes for a well-spaced generic array, but the ordering is unambiguous and physical.

## Slide 9
Physics-informed surrogate
Predict an unseen operating point’s full field in milliseconds
Maps (x, y, z, wind, discharge) to the velocity and temperature field.
Fourier features let a small network capture sharp plume gradients.
A mass-conservation (divergence-free) term is built into the loss.
Trained on six cases; the centre case was held out entirely.
1.62 K
temperature RMSE, unseen case
ms
inference vs a solver run
R² = 0.76 on temperature for an operating point the model never saw.

## Slide 10
Takeaways
Recirculation tracks the wind-to-plume balance: worst near 1.6%, best under 0.2%.
A converged 7-case CFD sweep, mass and energy balanced to better than 0.1%.
A physics-constrained surrogate reproduces an unseen field to 1.6 K in milliseconds.
The full pipeline, CFD to constrained learning, on a data-centre-adjacent thermal problem.
Limitations: coarse mesh with wall functions, steady RANS time-averaging, and a divergence constraint that is only part of the governing physics. Magnitudes are indicative; the trends and the workflow are the result.